## Slide 2: Chlorine Options… What’s Best for You? May 25, 2023 Dan Mohr

## Slide 3: 3 Major Sources of Chlorine
Gas Chlorine
Sodium Hypochlorite
Calcium Hypochlorite

## Slide 4: Chlorine Disinfectants:
Chlorine gas: Cl2 + H2O HCl + HOCl
Liquid Soda Bleach: NaOCl + H2O NaOH + HOCl
Calcium Hypochlorite: Ca(OCl)2 + 2 H2O Ca(OH)2 + 2 HOCl
(All three produce the same active sanitizer. HOCl Disinfects, Sanitizes and Residual Protection)

## Slide 5: Chlorine Disinfection Technologies
Chlorine Gas
Sodium Hypochlorite Liquid
On-site Generation (OSG)
Calcium Hypochlorite Tablets

## Slide 6: Chlorine System Applications
Primary Treatment
Remote Well Sites
Supplement for Ozone
Booster Stations for large networks
Wastewater Disinfection
Backup to UV

## Slide 7: Chlorine Gas
100% Available Chlorine
pH = 0.2
Cl2 (gas)
Stored in cylinders
Liquefied gas cooled under pressure

## Slide 8: Chlorine Gas Advantages
Excellent Residual Protection
Taste and odor control
Effective and accurate application
Lowest cost on per pound basis
No degradation upon storage

## Slide 9: Chlorine Gas Disadvantages
Safety concerns
Public awareness
Expensive auxiliary equipment
PSM/RMP administrative requirements
Manpower Costs
Liability
SCBA, Leak Detector, Automatic Shutoff Valves, Scrubbers, Annual
training.

## Slide 10: Sodium Hypochlorite

## Slide 11: Chlorine Delivered via Peristaltic Metering Pump

## Slide 12: Sodium Hypochlorite Disadvantages
Safe handling concerns- leaks, splash, & spills
Corrosive liquid & fumes – pH 13
Requires double containment
Scaling of injector due to high pH
Cumbersome to transport – 55 Gal Drum – 550Lbs
Off-gassing can cause vapor lock of pump
Higher material cost than gas chorine, $2.20 to $4.50 per gallon (Lb)

## Slide 13: Temperature Effects on the Decomposition of Liquid Bleach

## Slide 14: Drum vs Pail

## Slide 15: Bleach vs. Cal-Hypo: 3 MGD Treatment Plant

## Slide 16: Cracked Plastic Tubing

## Slide 17: On-site Hypochlorite Generation

## Slide 18: On-Site Hypo. Generator Advantages
Low hazards chlorine solution, 0.8% Cl2
No RMP reporting requirements
State-of-the-Art technology
No special emergency response training required

## Slide 20: On-Site Hypo. Generation Disadvantages
High capital cost, $20,000 for a 12#/day Unit
Requires salt storage; 3.5 lb/lb Cl2
Requires softening treatment of dilution water
Hydrogen gas off requires forced ventilation
System repair time could be lengthy depending on custom parts and problems, may need a back up chlorination system
Complex system requires high level of technical expertise
Cell efficiency is critical to operation

## Slide 21: Accu-Tab® System – Tablet Chlorination
PowerPro System 2075P System
MD System

## Slide 22: Accu-Tab® System
Accu-Tab® Tablet (calcium hypochlorite)
Accu-Tab® Chlorinator (erosion chamber)
Accu-Tab® PowerPro™ ,MD, or P System

## Slide 23: The Tablets - Accu-Tab® Tablets
Calcium Hypochlorite, 68.5% Cl2
325 grams
3 1/8” in diameter
Manufactured for controlled erosion
Scale Inhibitor (SI) - Phosphate
60 lb...Plastic Drums

## Slide 24: Accu-Tab Tablets
NSF 60 listed
Compact chemical storage
Dry, stable chlorine source
More neutral pH, less corrosive
No secondary containment
No risk management plans required

## Slide 25: The Chlorinator - Accu-Tab Chlorinators

## Slide 26: Accu-Tab Chlorinators
    The Accu-Tab® Chlorinator Advantage
    Engineered with rigid PVC
    Available in a variety of sizes
    Low maintenance
    Integrates easily with existing systems
    Durable Construction
    Accurate chlorine delivery

## Slide 27: How is the Chlorine delivered…

## Slide 28: Reduced Maintenance…Why?
Large orifices
Principal of dilution
Tablet technology
  Scale inhibitor
  Hard tablet
Self-flushing chlorinator design
Add no more than 1 week supply of tablets to chlorinator

## Slide 29: Setting Chlorine Dosage - Example
GPM X PPM X 0.0005 = lbs. Cl2/hr
Lbs. Cl2/hr X 1.5 = lbs. Tablets/hr
1500 gpm flow, 1.5 ppm total Cl2
1500gpm x 1.5ppm x 0.0005 = 1.12 lbs/hr Cl2
Go to 1.12 on the rate delivery chart ≈ 12 gpm of water through the chlorinator

## Slide 30: Chlorine Delivery Rate Chart

## Slide 31: Stacking Insert

## Slide 32: Delivery Rate with Stacking Cartridge

## Slide 33: PowerPro System

## Slide 34
Chlorinator
Solution tank
Water
Supply
Inlet
Filter
Chlorine
Solution
Out
Pump
Prime
Valve
Solenoid
Valve
HOA Switch
Discharge
Pump
Weight Scale
W/Low Tablet Alarm
Flow Meters and
Flow Control
Gate Valves
Discharge Flow
Gate Valve
Discharge
Check Valve
Electrical Box
And Panel
SYSTEM DESCRIPTION – POWERPRO
3 Phase
Disconnect
Pressure
Regulator
Hi Level
Sensor
Lo Level
Sensor
ATC 1000
Float
Valve

## Slide 35
Chlorinator
Solution tank
Water
Supply
Inlet
Filter
Chlorine
Solution
Out
Pump
Prime
Valve
Solenoid
Valve
HOA Switch
Discharge
Pump
Weight Scale
W/Low Tablet Alarm
Flow Meters and
Flow Control
Gate Valves
Discharge Flow
Gate Valve
Discharge
Check Valve
Electrical Box
And Panel
SYSTEM DESCRIPTION – POWERPRO
3 Phase
Disconnect
Pressure
Regulator
Hi Level
Sensor
Lo Level
Sensor
ATC 1000
Float
Valve

## Slide 36: Power Pro® System Options
Controller Integrated
  Flow pacing control
  Residual control
  Compound loop control
SCADA ready
Tablet scale*
Low tablet scale alarm*

## Slide 37: Detailed Component Description
Accu-Tab® PowerPro® System
Supply Water Line - Inlet Strainer
Pressure Regulator

## Slide 38
Diluted Hypochlorite Solution Tank
Supply Water In
Cl2 Feed to System
Process
Controller
PowerPro System
Notes: Simple. Water in Water out.

## Slide 39
Hand/Off/Auto
Switch
Digital
Readout
Disconnect
Switch
PowerPro System

## Slide 40
Flow Control Valve
Inlet Flow Meter
Chlorine Dosage Adjustment
Notes: 40
Simple. Water in Water out.

## Slide 41
Aluminum
Frame
Brass
Solenoid
Valve
Injection Pump
3” Calcium Hypochlorite Tablet Eroder

## Slide 42: Solution Tank Internals
Hi Level
Solenoid
Shutoff
Lo Level
Pump
Shutoff
Float Valve
Tank Drain

## Slide 43: PowerPro Dilution Water Inlet

## Slide 44
Vertically Mounted Grundfos
Pump with VFD
Tablet
Scale

## Slide 45: Digital Weigh Scale

## Slide 46: PowerPro Power Board

## Slide 47: PowerPro Display Board

## Slide 48: Accu-Tab® PowerPro MD System
Batch System
Constant Solution
Strength
Multiple Injection
Points Available
Very High Turn
Down Ratio

## Slide 49
Chlorinator
Solution tank
Water
Supply
Inlet
Filter
Chlorine
Solution
Out
Pump
Prime
Valve
Solenoid
Valve
HOA Switch
Discharge
Pump
Weight Scale
W/Low Tablet Alarm
Flow Meters and
Flow Control
Gate Valves
Discharge Flow
Control Gate Valve
Discharge
Check Valve
Electrical Box
And Panel
SYSTEM DESCRIPTION – POWERPRO MD
Discharge Flow Meter
Field Installed
3 Phase
Disconnect
Ultrasonic
Level Sensor
Pressure
Regulator
FM
Hi Level Sensor
Lo Level Sensor
Lo Lo Level Sensor
ATC 1000
Hi Hi Level Sensor

## Slide 50: PowerPro MD System
Chlorine Flow
Control Valve
Chlorinator Flow
Indicator
By-pass Water Flow
Control Valve
By-pass flow meter

## Slide 51: By-pass flowmeter and flow control valve

## Slide 52
PowerPro MD
Outlet Discharge
Manifold
Discharge Flow Meters
Discharge Flow
Control Valves
Discharge Automatic
On/Off Valves
Discharge Check Valves

## Slide 53: Accu-Tab 2000P System
Skid-mounted
Simple ‘plug-and-play’ installation
Provides efficient, controllable chlorine delivery
Low capital costs
Minimal maintenance
Notes: Custom build to meet the requirements of the system.

## Slide 54: Accu-Tab 2000P Models
2075P– up to 2.5 lbs/hr
2150P – up to 10.5 lbs/hr

## Slide 55: Accu-Tab 2000P Diagram

## Slide 56: 2000P Options
WEG VFD for…
  Flow pacing
  Residual control
  Compound loop control
2000 Series Controller
Tablet Weigh Scale

## Slide 57: Accu-Tab 2000 Controller

## Slide 58: WEG Stand Alone VFD

## Slide 59: Chlorine Residual Results Residual Control

## Slide 60: Economic Analysis Tool

## Slide 61: Initial Capital Cost Comparison

## Slide 62: Total Cost Comparison

## Slide 63: In Review
Cal Hypo Tablets are a solid alternative
Reduces safety and handling concerns
Eliminate hidden chlorination costs
Provide safe, accurate, and reliable
chlorination
Cost effective – Use economic analysis tool

## Slide 64: System Capabilities
Flow pacing control
Residual control
Compound loop control
SCADA ready
Hi/Lo level alarms
Tablet scale
Low tablet alarm
220 single/three Phase or 460 3 phase power
Multiple Cl2 Injection Points

## Slide 65: Approvals & Standards:
NSF Standard 60/61 (drinking water) certified
USDA approved uses:
  G-4, G-5, G-7, D-2, and Q-4
Meets AWWA Standard B-300
EPA Registration #748-295

## Slide 66
www.accu-tab.com

## Slide 67
Water Solutions
Questions ?
Dan Mohr
713-299-8641
dmohr@Westlake.com