## Slide 1: 2023 Hawaii Rural Water Association Optimal Application of Pipe Bursting and Trenchless Methods - 9,000 feet of both Water and Sewer Pipeline in the City of Eureka, CA
George Mallakis
TT Technologies, Inc.
Mike Garrett
Underground Solutions, Inc

## Slide 2: City of Eureka, CA
Largest coastal city between
San Francisco and Portland Oregon
Located on US Route 101 on the shores of Humboldt Bay and adjacent to CA’s Redwood Forest
Population of approximately 28,000

## Slide 3: Public Works Department
Engineering and Field Operations
Water Distribution and Wastewater Systems
Designed the Henderson
Water and Sewer
Improvements Project and
Bid November 19, 2020

## Slide 4: Project Design Details
3,600 feet of sewer mains and 41 sewer service laterals
5,000 feet of water mains and 34 water service laterals
“Open Cut” existing water mains and install new Ductile Iron Pipe
“Open Cut” existing sewer mains and install new PVC Pipe
Use “Trenchless” to replace water and sewer service laterals

## Slide 5: Bid Results
Mercer Fraser Co - $3,025,882
Bidder #2 - $3,825,213
Bidder #3 - $3,889,783
Mercer Fraser planned to use pipe bursting which cost less saving the city $800,000 or 25% over next lowest bidder

## Slide 6
Pipe Bursting Line Items Open Cut Pricing
Mercer Fraser Bidder #2 Bidder #3
8-inch water per lf $75 $158 $178
8-inch sewer per lf $105 $180 $198

## Slide 7: Post Bid Details
Contractor and City had experience using Pipe Bursting
  Benefits: Pipe Bursting will minimize disruption, reduce carbon emissions,
  increase productivity and save money.
Pipe Bursting Scope became…
3,600’ of existing 8” VCP sewer pulling in new 8” HDPE
5,000’ of existing 8” ACP and CIP pipe pulling in new 8” FPVC

## Slide 8: Construction
New Pipe Materials used:
Water Mains – Fusible PVC (FPVC)
Sewer Mains – High Density Polyethene (HDPE)
Both great materials – city was familiar with each of these
pipe products used in past water and sewer projects

## Slide 9: Construction
Equipment Choices
TT Technologies, Inc. Grundoburst Static Pipe Bursting System
Contractor familiar and experienced with this equipment used on previous projects
Accommodates all existing and new pipe materials
Compact, quiet, and productive

## Slide 10: Equipment

## Slide 11: Construction – Water Mains
Temporary Bypass System (Sideline) for Services

## Slide 12: Construction – Water Mains
Temporary Bypass System (Sideline) for Services

## Slide 13: Construction – Water Mains
FPVC Pipe Fusion

## Slide 14
Excavations and Pipe Bursting
Set Up - Water

## Slide 15
Pipe Bursting - Water

## Slide 16
Water Main - reconnects

## Slide 17
Water Main - resurfacing
Open Cut
Pipe Bursting

## Slide 18: Construction – Sewer Mains
Temporary Bypass System

## Slide 19
Excavations and Pipe Bursting Set Up – Sewer

## Slide 20
Sewer main - reconnects

## Slide 21
Sewer Main - resurfacing

## Slide 22
Trenchless Water Service Replacements

## Slide 23
Trenchless Sewer Service Replacements

## Slide 24: Pipe Bursting Productions
Pipe Runs: 180-feet to 350-feet lengths of pipe
1 to 2 runs per day
About 3 hours to push out rod and pull back 300 feet
Reconnect, backfill, and pave each day
8 - person crew (3 - persons Pipe Burst, others prep & close)
7:30 am to 3:30 pm (8 - hour workdays)
Extremely efficient Contractor and Crew

## Slide 25: Summary
Trenchless method of Pipe Bursting:
Applicable to both water and sewer
Apply to not only mainlines but, also service laterals
Choices available for new pipe materials and fittings
Productive, less disruptive, less emissions, and less expensive than open cut
Savings of 25% - $800,000 in this case

## Slide 26: Questions?
George Mallakis
TT Technologies, Inc.
Mike Garrett
Underground Solutions, Inc